BID SPECIFICATION SHEET FOR FB16-032

INSTALLATION OF DAIKIN HEAT SYSTEM in LOONEY

Scope:

Remove existing rooftop air handling unit and associated condenser and install new rooftop package air conditioner. Contact Gregory George at the Physical Plant Department 816-271-4417 to view project site, obtain engineered drawings and specifics of installation.  Direct all other questions to Purchasing Manager, Kelly Sloan (816) 271-4465, purchase@missouriwestern.edu

Timeline of Project:

- Mandatory pre-bid meeting at Physical Plant breakroom Aug. 20th at 10:00am

- Bid opening August 27, 2015 2:00pm Purchasing Department, Popplewell 221

- Project to be completed by October 9, 2015

Bid Specification:

- Installation shall include all mechanical and electrical aspects necessary for completion of the project.

- MWSU will provide Daikin’s model MPS050FE unit and associated “MicroTech III” remote user interface.

- Installation is to be performed in strict accordance with the manufacturer’s installation instructions.

- MWSU will provide the adapting curb to facilitate connection from unit to existing ductwork.

- All work shall conform to all applicable building codes.

- Condenser’s existing 2/0 THWN power wiring is to be salvaged and reused to power the new RTU.

- Condenser’s existing electrical conduits and refrigeration piping are to be removed.

- Contractor is to supply and install a new “Square D” 175 amp, 3 pole, (10,000 AIC min) circuit breaker into existing panel.

- Contractor is to install new 1-1/2”EMT raceway to new unit and install three salvaged 2/0 and new 6AWG conductors into it.

- Low voltage connection to the remote interface is to be contractor’s option of manufacturer’s methods that will provide minimum distance mounting of 700m.

- Installation hall be subject to guidance/oversight and inspection by representatives of Thermal Mechanics Inc.

- All work is to be performed in accordance with MWSU’s “Hot Work” guidelines.

- Contractor shall warrant their workmanship and provided materials for a period of one year from date of acceptance.

- This will be a prevailing wage project.

- Bidders must submit a notarized Affidavit of Work Authorization and completed MOU signature pages, per attached memorandum dated January 2014, with their bids.

- Annual Wage Order Number 22 is currently in effect.  A copy of this order will be attached separately once bid is awarded.

- A Certificate of Liability Insurance will be required with MWSU listed as an additional insured.

- Missouri Revised Statute Chapter 292.675 went into effect on August 28, 2008, all on-site employees are required to complete the ten-hour safety training program and must provide proof if requested by showing training card.

Bid Amount $ _______________________________

Company _________________________________________________

Phone Number:________________________________________________

Authorized Signature 						   Date ______________

Return this pricing sheet with your bid.  Include any addendum(s) with your initials.

Pricing must be FOB Missouri Western State University.

All questions should be directed to Purchasing Manager, Kelly Sloan, (816) 271-4465, purchase@missouriwestern.edu

Missouri Western reserves the right to accept or reject any or all items of this bid.

Include with your bid:

- Notarized Affidavit of Work Authorization (see attached), completed MOU signature pages and insurance.

PREVAILING WAGE PROJECT INFORMATION

TO:			ALL BIDDERS

FROM:           	MISSOURI WESTERN STATE UNIVERSITY

DATE:  		January 2014

RE:			ADDITIONAL BID SUBMISSION REQUIREMENTS

Please review Missouri statute, 285.530 RSMo, regarding employment of unauthorized aliens. Pursuant to RSMo 285.530 (1), No business entity or employer shall knowingly employ, hire for employment, or continue to employ an unauthorized alien to perform work within the State of Missouri, and (2), the bidder must affirm its enrollment and participation in a federal work authorization program with respect to the employees proposed to work in connection with the services requested herein by:

Submitting a completed, notarized copy of AFFIDAVIT OF WORK AUTHORIZATION (attached) and,

Providing documentation affirming the bidder’s enrollment and participation in a federal work authorization program (see below) with respect to the employees proposed to work in connection with the services requested herein.

A copy of RSMo 285.530 can be viewed in its entirety at:

http://www.moga.mo.gov/statutes/C200-299/2850000530.HTM

E-Verify is an example of a federal work authorization program.  Acceptable enrollment and participation documentation consists of completed copy of the E-Verify Memorandum of Understanding (MOU).  A sample of the MOU is included.   For vendors that are not already enrolled and participating in a federal work authorization program, E-Verify is available at:

http://www.dhs.gov/files/programs/gc_1185221678150.shtm

The successful bidder will be required to submit a notarized Affidavit of Work Authorization and the completed MOU signature pages (the last three pages) with their bid.  A bid that does not include these items will be deemed Non-responsive.

# WORK AUTHORIZATION AFFIDAVIT

# PURSUANT TO R.S.Mo. §285.530

# (For all bids in excess of $5,000.00)

# Effective 1/1/09

State of Missouri		)

)ss

County of Buchanan		)

Comes now ________________________________ (Name of Business Entity Authorized Representative) as _____________________ (Position/Title) first being duly sworn on my oath, affirm __________________________ (Business Entity Name) is enrolled and will continue to participate in the E-Verify federal work authorization program with respect to employees hired after enrollment in the program who are proposed to work in connection with the services related to contract(s) with the State of Missouri for the duration of the contract(s), if awarded in accordance with subsection 2 of section 285.530, RSMo.  I also affirm that ____________________________ (Business Entity Name) does not and will not knowingly employ a person who is an unauthorized alien in connection with the contracted services provided under the contract(s) for the duration of the contract(s), if awarded.

In Affirmation thereof, the facts stated above are true and correct.  (The undersigned understands that false statements made in this filing are subject to the penalties provided under section 575.040, RSMo.)

| Authorized Representative’s Signature |  | Printed Name |
| --- | --- | --- |
| Title |  | Date |
| E-Mail Address |  | E-Verify Company ID Number |

Subscribed and sworn to before me this _____________ of ___________________.  I am

(DAY)		(MONTH, YEAR)

commissioned as a notary public within the County of _____________________, State of

(NAME OF COUNTY)

_______________________, and my commission expires on _________________.

(NAME OF STATE)						(DATE)

| Signature of Notary |  | Date |
| --- | --- | --- |